## VPP_Units
VPP PARAMETERS | DESCRIPTION | [8 empty] | VPP PARAMETERS | DESCRIPTION
ID | \\ Identification of VPP unit for indexing | [8 empty] | RegUpCost | \\ Up regulation cost of VPP unit [€]
BusNumber | \\ Bus location to which the VPP unit is connected | [8 empty] | RegDownCost | \\ Down regulation cost of VPP unit [€]
Pmax | \\ Maximum active power capacity of VPP unit [MW] | [8 empty] | DamCost | \\ Operation cost of VPP unit during DAM participation [€]
Pmin | \\ Minimum active capacity of VPP unit [MW] | [8 empty] | EtMin | \\ Minimum overall consumption of demand unit over participation horizon [MWh]
Qmax | \\ Maximum reactive power capacity of VPP unit [MW] | [8 empty] | UnitType | \\ Keyword stating whether VPP unit is a generator [G], demand [D] or ESS unit [E]
Qmin | \\ Minimum reactive capacity of VPP unit [MW] | [8 empty] | DeltaFss | \\ Post‐disturbance steady‐state frequency deviation [%]
Gen0 | \\ Active power generated by VPP unit before 1st period [MW] | [8 empty] | Inertia | \\ Amount of inertia to be provided by VPP unit [%]
RampUp | \\ Active power ramp up [MW] | [8 empty] | EssChCap | \\ Charge capacity of Energy Storage System [MW]
RampStartup | \\ Startup ramp [MW] | [8 empty] | EssDisCap | \\ Discharge capacity of Energy Storage System [MW]
Gen0Commit | \\ Commitment status of the VPP unit before 1st period [-] | [8 empty] | EssChEff | \\ Charging efficiency of Energy Storage system [%]
RampDown | \\ Active power ramp down [MW] | [8 empty] | EssDisEff | \\ Discharging efficiency of Energy Storage System [%]
RampShutdown | \\ Shutdown ramp [MW]
ID | BusNumber | Pmax | Pmin | Qmax | Qmin | RampUp | RampStartup | RampDown | RampShutdown | Gen0Commit | Gen0 | RegUpCost | RegDownCost | DamCost | EtMin | DeltaFss | Inertia | EssChCap | EssDisCap | EssChEff | EssDisEff | Units | UnitType
WPP | B2 | 50 | 0 | 30 | -30 | 50 | 50 | 50 | 50 | 1 | 50 | 2 | 2 | 10 | 0 | 0.08 | 0.1 | 0 | 0 | 0 | 0 | WPP | G
PV | B6 | 50 | 0 | 30 | -30 | 50 | 50 | 50 | 50 | 1 | 50 | 3 | 3 | 10 | 0 | 0.08 | 0.1 | 0 | 0 | 0 | 0 | PV | G
STU | B5 | 50 | 0 | 30 | -30 | 50 | 50 | 50 | 50 | 1 | 50 | 4 | 4 | 15 | 0 | 0.08 | 0.1 | 0 | 0 | 0 | 0 | STU | G
TES | B5 | 0 | 0 | 30 | -30 | 0 | 0 | 0 | 0 | 1 | 0 | 4 | 4 | 15 | 0 | 0.08 | 0.1 | 140 | 115 | 0.9 | 0.9 | TES | E
F-DEM | B3 | 30 | 0 | 30 | -30 | 30 | 30 | 30 | 30 | 1 | 30 | 6 | 6 | 17.5 | 0 | 0.08 | 0.1 | 0 | 0 | 0 | 0 | F-DEM | D

## Global_params
GLOBAL PARAMETERS | DESCRIPTION
Period | \\ Number of periods used in energy markets |  |  |  |  | EmCost | \\ Energy market price [€]
SubPeriod | \\ Number of subdivisions for real time optimization |  |  |  |  | PmCost | \\ Primary frequency control market price [€]
PenaltyCost | \\ Penalty cost for not fulfilling TSO requirement [€] |  |  |  |  | ImCost | \\ Inertia market price [€]
TsoCommand | \\ TSO command for AGC request [MW]
SolverSelect | \\ Select which program to run according to key below |  |  |  |  | IpfcMode | \\ Set this scalar to select mode of IPFC service
| 1. DC power flow for inertia and PFC service (IPFC_DCOPF) | [5 empty] | 1. Compulsory: each unit provides the minimum PFC
| 2. AC power flow for inertia and PFC service (IPFC_ACOPF) | [5 empty] | 2. Overall PFC provided on VPP basis (some units can provide more\less than offered)
3. DC power flow for aFRR (RTM_DCOPF)
| 4. AC power flow for aFRR (RTM_ACOPF) |  |  |  |  | Gamma | \\ Self discharge rate of BESS
PowerBase | \\ Base apparent power [MVA] |  |  |  |  | EssLbFinal | \\ Lower bound multiplier for ESS at final period
[6 empty] | Lambda | \\ Cost to avoid simultaneous up/down reg provision at same period [€]
Period | SubPeriod | Mod | Mod | PenaltyCost | TsoCommand | SolverSelect | EmCost | PmCost | ImCost | IpfcMode | Gamma | EssLbFinal | Lambda | PowerBase
96 | 60 | 0 | 0 | 750 | 0 | 3 | 22.5 | 30 | 25 | 1 | 0 | 0 | 500 | 100

## Buses
BUS PARAMETERS | DESCRIPTION
ID | \\ Identification of bus for indexing
BusType | \\ Specification for distribution or transmission bus
BusName | \\ Name of the bus
BaseKV | \\ Base kilo volt for computation in per unit [kV]
Code | \\ Code depicting if the bus is slack, PQ or PV
NormalVmax | \\ Normal maximum voltage in each bus in per unit
NormalVmin | \\ Normal minimum voltage in each bus in per unit
EmergencyVmax | \\ Emergency maximum voltage in each bus in per unit
EmergencyVmin | \\ Emergency minimum voltage in each bus in per unit
ID | BusType | BusName | BaseKV | Code | NormalVmax | NormalVmin | EmergencyVmax | EmergencyVmin
B1 | T | B1 | 132 | 3 | 1.1 | 0.95 | 1.1 | 0.9
B2 | C | B2 | 66 | 1 | 1.1 | 0.95 | 1.1 | 0.9
B3 | C | B3 | 66 | 1 | 1.1 | 0.95 | 1.1 | 0.9
B4 | C | B4 | 66 | 1 | 1.1 | 0.95 | 1.1 | 0.9
B5 | C | B5 | 66 | 1 | 1.1 | 0.95 | 1.1 | 0.9
B6 | C | B6 | 66 | 1 | 1.1 | 0.95 | 1.1 | 0.9
B7 | C | B7 | 20 | 2 | 1.1 | 0.95 | 1.1 | 0.9

## Branches_Lines
BRANCH PARAMETERS | DESCRIPTION
FromBusNumber | \\ Origin bus for line
ToBusNumber | \\ Destination bus for line
LineR | \\ Resistance of line [pu]
LineX | \\ Reactance of line [pu]
ChargingB | \\ Charging susceptance of line [pu]
InService | \\ Status of line. '1' if line is in service, '0' if line is out of service [-]
Rate1 | \\ Line rating [MVA]
Rate2 | \\ Line rating [MVA]
Rate3 | \\ Line rating [MVA]
FromBusNumber | ToBusNumber | LineR | LineX | ChargingB | InService | Rate1 | Rate2 | Rate3
B1 | B4 | 0.012 | 0.05 | 0.0014 | 1 | 200 | 100 | 100
B4 | B3 | 0.012 | 0.0721 | 0.0014 | 1 | 200 | 100 | 100
B4 | B6 | 0.012 | 0.0721 | 0.0014 | 1 | 200 | 100 | 100
B4 | B2 | 0.012 | 0.0721 | 0.0014 | 1 | 200 | 100 | 100
B4 | B5 | 0.01 | 0.05 | 0 | 1 | 200 | 200 | 200
B5 | B6 | 0.01 | 0.03 | 0 | 1 | 200 | 200 | 200
B2 | B5 | 0.016 | 0.048 | 0 | 1 | 200 | 125 | 125
B5 | B7 | 0.012 | 0.0721 | 0 | 1 | 200 | 125 | 125

## Bus_trade
BUS PARAMETERS | DESCRIPTION
TradedPower | \\ Traded power in the bus connected to the transmission grid [MW]
UpSrOffer | \\ Up regulation offer for secondary reserve provision [MW]
DownSrOffer | \\ Down regulation offer for secondary reserve provision [MW]
ID | Period | TradedPower | UpSrOffer | DownSrOffer | PAvailable | QLoad
B1 | 1 | -2.6651 | 9.237 | 7.8949
B1 | 2 | -0.761 | 9.741 | 8.3256
B1 | 3 | 5.728 | 10.812 | 8.6496
B1 | 4 | 8.584 | 11.316 | 9.0528
B1 | 5 | 10.0035 | 11.5665 | 9.2532
B1 | 6 | 6.7775 | 11.0925 | 8.874
B1 | 7 | 8.1885 | 11.3415 | 6.3008
B1 | 8 | 4.838 | 10.782 | 5.99
B1 | 9 | 20.4525 | 13.5375 | 7.5208
B1 | 10 | 24.9935 | 14.1165 | 7.8425
B1 | 11 | 50.2351 | 14.595 | 12.1625
B1 | 12 | 73.0175 | 14.1525 | 11.7937
B1 | 13 | 70.4505 | 13.6995 | 11.4162
B1 | 14 | 73.4265 | 14.2035 | 11.8363
B1 | 15 | 73.7665 | 14.2635 | 11.8863
B1 | 16 | 59.048 | 14.58 | 12.15
B1 | 17 | 60.0928 | 13.6291 | 11.3576
B1 | 18 | 63.9165 | 12.6735 | 10.5612
B1 | 19 | 60.947 | 11.673 | 9.7275
B1 | 20 | 41.58 | 2.34 | 1.3
B1 | 21 | 46.2 | 1.74 | 0.96667
B1 | 22 | 50.08 | 1.44 | 1.2632
B1 | 23 | 40.4016 | 9.1065 | 7.9882
B1 | 24 | 37.411 | 8.649 | 6.503

## Dispatches
DISPATCH PARAMETERS | DESCRIPTION
ID | \\ Identification of VPP unit for indexing
Period | \\ Period utilized in energy market scheduling
Commitment | \\ Commitment status of VPP unit at each period [-]
Pgen | \\ Generation/consumption of VPP unit in each period [MW]
StartUp | \\ Start up status of VPP unit [-]
ShutDown | \\ Shutdown status of VPP unit [-] | [12 empty] | Sta | Dyn
RegMaxUp | \\ Maximum up regulation that VPP unit can provide [MW]
RegMaxDown | \\ Maximum down regulation that VPP unit can provide [MW] | [10 empty] | G2 | DG | 31.5 | 38.18 | 0.82504
RegMaxUpV2 | \\ Maximum up regulation that VPP unit can provide_version 2 [MW] | [10 empty] | G3 | PV | 43 | 49.68 | 0.86554
RegMaxDownV2 | \\ Maximum down regulation that VPP unit can provide_version 2 [MW] | [10 empty] | G5 | WPP | 17 | 23.68 | 0.71791
PAvailable | \\ Available real time generation of stochastic RES units [MW]
QLoad | \\ Reactive power consumption of VPP demand units [Mvar]
ID | Period | Commitment | Pgen | StartUp | ShutDown | RegMaxUp | RegMaxDown | RegMaxUpV2 | RegMaxDownV2 | PAvailable | QLoad
STU | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STU | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STU | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STU | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STU | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STU | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STU | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STU | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STU | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STU | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STU | 11 | 1 | 9.8551 | 1 | 0 | 14.595 | 0 | 0 | 4.1551
STU | 12 | 1 | 49.8 | 0 | 0 | 0 | 0 | 0 | 0
STU | 13 | 1 | 49.8 | 0 | 0 | 0 | 0 | 0 | 0
STU | 14 | 1 | 49.8 | 0 | 0 | 0 | 0 | 0 | 0
STU | 15 | 1 | 49.8 | 0 | 0 | 0 | 0 | 0 | 0
STU | 16 | 1 | 33.288 | 0 | 0 | 0 | 0 | 0 | 0
STU | 17 | 1 | 40.252 | 0 | 0 | 0 | 0 | 0 | 0
STU | 18 | 1 | 49.8 | 0 | 0 | 0 | 0 | 0 | 0
STU | 19 | 1 | 40.467 | 0 | 0 | 9.333 | 0 | 0 | 0
STU | 20 | 1 | 44.6 | 0 | 0 | 0 | 0 | 0 | 0
STU | 21 | 1 | 44.6 | 0 | 0 | 0 | 0 | 0 | 0
STU | 22 | 1 | 44.6 | 0 | 0 | 0 | 0 | 0 | 0
STU | 23 | 1 | 40.3401 | 0 | 0 | 4.2599 | 0 | 0 | 0
STU | 24 | 1 | 35.951 | 0 | 0 | 8.649 | 0 | 0 | 0
TES | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TES | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 1 | 1 | 9.6 | 0 | 0 | 0.95187 | 0 | 0 | 0.96
F-DEM | 2 | 1 | 9.6 | 0 | 0 | 0 | 0 | 0 | 0.96
F-DEM | 3 | 1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 4 | 1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0.54
F-DEM | 5 | 1 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 6 | 1 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 7 | 1 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 8 | 1 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 9 | 1 | 12.6 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 10 | 1 | 18.6 | 0 | 0 | 1.86 | 0 | 0 | 0
F-DEM | 11 | 1 | 19.2 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 12 | 1 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 13 | 1 | 19.8 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 14 | 1 | 18.6 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 15 | 1 | 18.6 | 0 | 0 | 0 | 0 | 0 | 1.7963
F-DEM | 16 | 1 | 18.6 | 0 | 0 | 0 | 0 | 0 | 1.86
F-DEM | 17 | 1 | 23.91 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 18 | 1 | 27 | 0 | 0 | 0 | 0 | 0 | 0
F-DEM | 19 | 1 | 23.4 | 0 | 0 | 2.34 | 0 | 0 | 2.34
F-DEM | 20 | 1 | 23.4 | 0 | 0 | 2.34 | 0 | 2.34 | 0
F-DEM | 21 | 1 | 17.4 | 0 | 0 | 1.74 | 0 | 0 | 0.96667
F-DEM | 22 | 1 | 14.4 | 0 | 0 | 1.44 | 0 | 0 | 1.2632
F-DEM | 23 | 1 | 14.4 | 0 | 0 | 0.63813 | 0 | 0 | 0
F-DEM | 24 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 1.2
WPP | 1 | 1 | 6.9349 | 0 | 0 | 8.2851 | 0 | 0 | 6.9349
WPP | 2 | 1 | 8.839 | 0 | 0 | 9.741 | 0 | 0 | 7.3656
WPP | 3 | 1 | 11.128 | 0 | 0 | 10.812 | 0 | 0 | 8.6496
WPP | 4 | 1 | 13.984 | 0 | 0 | 11.316 | 0 | 0 | 8.5128
WPP | 5 | 1 | 15.4035 | 0 | 0 | 11.5665 | 0 | 0 | 9.2532
WPP | 6 | 1 | 17.5575 | 0 | 0 | 11.0925 | 0 | 0 | 8.874
WPP | 7 | 1 | 18.9885 | 0 | 0 | 11.3415 | 0 | 0 | 6.3008
WPP | 8 | 1 | 16.118 | 0 | 0 | 10.782 | 0 | 0 | 5.99
WPP | 9 | 1 | 22.87 | 0 | 0 | 0 | 0 | 0 | 7.5208
WPP | 10 | 1 | 7.8425 | 0 | 0 | 10.9975 | 0 | 0 | 7.8425
WPP | 11 | 1 | 16.93 | 0 | 0 | 0 | 0 | 0 | 0
WPP | 12 | 1 | 11.71 | 0 | 0 | 0 | 0 | 0 | 0
WPP | 13 | 1 | 8.13 | 0 | 0 | 0 | 0 | 0 | 0
WPP | 14 | 1 | 0 | 0 | 0 | 9.11 | 0 | 9.11 | 0
WPP | 15 | 1 | 10.09 | 0 | 0 | 0 | 0 | 0 | 10.09
WPP | 16 | 1 | 10.29 | 0 | 0 | 2.52 | 0 | 0 | 10.29
WPP | 17 | 1 | 13.27 | 0 | 0 | 0 | 0 | 0 | 0
WPP | 18 | 1 | 13.74 | 0 | 0 | 0 | 0 | 0 | 0
WPP | 19 | 1 | 14.19 | 0 | 0 | 0 | 0 | 0 | 7.3875
WPP | 20 | 1 | 16.48 | 0 | 0 | 0 | 0 | 0 | 0
WPP | 21 | 1 | 19 | 0 | 0 | 0 | 0 | 0 | 0
WPP | 22 | 1 | 19.88 | 0 | 0 | 0 | 0 | 0 | 0
WPP | 23 | 1 | 14.4615 | 0 | 0 | 4.2085 | 0 | 0 | 7.9882
WPP | 24 | 1 | 13.46 | 0 | 0 | 0 | 0 | 0 | 5.303
PV | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV | 6 | 1 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0
PV | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV | 8 | 1 | 1.32 | 0 | 0 | 0 | 0 | 0 | 0
PV | 9 | 1 | 10.1825 | 0 | 0 | 13.5375 | 0 | 0 | 0
PV | 10 | 1 | 35.751 | 0 | 0 | 1.259 | 0 | 0 | 0
PV | 11 | 1 | 42.65 | 0 | 0 | 0 | 0 | 0 | 8.0074
PV | 12 | 1 | 31.3075 | 0 | 0 | 14.1525 | 0 | 0 | 11.7937
PV | 13 | 1 | 32.3205 | 0 | 0 | 13.6995 | 0 | 0 | 11.4163
PV | 14 | 1 | 42.2265 | 0 | 0 | 5.0935 | 0 | 0 | 20.9463
PV | 15 | 1 | 32.4765 | 0 | 0 | 14.2635 | 0 | 0 | 0
PV | 16 | 1 | 34.07 | 0 | 0 | 12.06 | 0 | 0 | 0 |  |  | 12.06 | regmaxup
PV | 17 | 1 | 30.4809 | 0 | 0 | 13.6291 | 0 | 0 | 11.3576
PV | 18 | 1 | 27.3765 | 0 | 0 | 12.6735 | 0 | 0 | 10.5613
PV | 19 | 1 | 29.69 | 0 | 0 | 0 | 0 | 0 | 0
PV | 20 | 1 | 3.9 | 0 | 0 | 0 | 0 | 0 | 3.64
PV | 21 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV | 22 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV | 23 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PV | 24 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## AC-PF-LTVM (hidden)
Conversion Status | Dispatches |  |  |  |  | Voltage Magnitudes |  | Branch Flows [MW]
1
| Generator ID | Active Power Gen [MW] | PFC [MW] | Inertia [MW] | Reactive Power Gen [MVar] | Bus number | Voltage [V] | From bus | To bus | Active Power Flow [MW] | Reactive Power Flow [MW] | Line Rating Result [MVA] | Line Rating Actual [MVA] | % of Line Rating
vGrid_P | ESS | -12.8 | 3.2 | 4 | 30 | 1 | 1 | 1 | 10 | 86.5746 | 79.1729 | 117.318 | 200 | 58.659
106.2457 | PV | 12.8 | 12.8 | 16 | -55.9455 | 10 | 1.0494 | 10 | 1 | -86.5746 | -79.1729 | 117.318 | 200 | 58.659
| DG1 | 30 | 3.2 | 4 | 8.4284 | 11 | 1.0865 | 10 | 11 | 91.2467 | 32.8544 | 96.9813 | 100 | 96.9813
| DG2 | 0 | 0 | 0 | -30 | 12 | 1.1 | 10 | 13 | -5.6485 | 40.9274 | 41.3153 | 100 | 41.3153
vGrid_Q | [5 empty] | 13 | 1.0802 | 11 | 10 | -91.2467 | -33.0127 | 97.035 | 100 | 97.035
81.5281 | [5 empty] | 14 | 1.0938 | 11 | 12 | 90.3671 | 2.0394 | 90.3901 | 100 | 90.3901
[6 empty] | 21 | 1.095 | 11 | 21 | 0.042374 | 26.0726 | 26.0726 | 200 | 13.0363
[6 empty] | 22 | 1.1 | 12 | 11 | -90.3671 | -2.2044 | 90.394 | 100 | 90.394
[8 empty] | 13 | 10 | 5.6485 | -41.085 | 41.4714 | 100 | 41.4714
[8 empty] | 13 | 14 | -29.7911 | 22.2293 | 37.1706 | 100 | 37.1706
[8 empty] | 14 | 13 | 29.7911 | -22.3926 | 37.2685 | 100 | 37.2685
[8 empty] | 14 | 22 | -29.9281 | 21.7874 | 37.0186 | 125 | 29.6149
[8 empty] | 21 | 11 | -0.042374 | -26.0726 | 26.0726 | 200 | 13.0363
[8 empty] | 22 | 14 | 29.9281 | -21.7874 | 37.0186 | 125 | 29.6149